## Sheet1
গণপ্রজাতন্ত্রী বাংলাদেশ সরকার
শ্রম ও কর্মসংস্থান মন্ত্রণালয়
কলকারখানা ও প্রতিষ্ঠান পরিদর্শন অধিদপ্তর
প্রতিষ্ঠানসমূহের তালিকা
কারখানার নাম | এসোসিয়েট ইন্ডা: প্রা: লি:
কারখানার ঠিকানা | , 0,( konabari, Gazipur, Dhaka )
মূল্যায়নের ধরণ | বৈদ্যুতিক মূল্যায়ন
মূল্যায়নের তারিখ | ১২-০৯-২০২১
পর্যবেক্ষণের তারিখ
পরিদর্শন পর্যবেক্ষণ | কর্ম পরিকল্পনা | চূড়ান্ত কর্ম পরিকল্পনা | চূড়ান্ত সময়রেখা | মন্তব্য | অগ্রগতির অবস্থা
Electrical Single Line Diagram was not available in the factory. | a. Provide updated SLD matching the existing installation at the factory. b. SLD to indicate exact positions of all points of switch boxes and other outlets. c. SLD to be approved by the engineer-in-charge.
As built Electrical Layout Drawings’ was not available in the factory. | a. Provide updated Electrical layout drawing prepared after proper locations of all outlets for lamps, fans, fixed and transportable appliances, motors etc. b. Drawings to indicate exact positions of all points of switch boxes and other outlets to match existing installation. c. As built drawing to be approved by the engineer-in-charge.
Adequate ventilation system was not available in generator room. | Provide adequate ventilation arrangements for indoor substation.
Rubber mats were not provided in front of distribution board.. | Provide rubber mats in front of all distribution panels.
Fire protection (Smoke detector) was not provided in Generator room | Install smoke detection and provide firefighting equipment in the substation and generator room.
Generator was located in separate building but near to exit stair, fire door/wall was not available. | Provide 4 hour fire rated walls all around the transformer / generator room on ground level.
COS was used as LT panel, there was no permanently labeled/marked for identifications. | Provide and maintain clear and legible identifications numbers & names on all incoming and outgoing circuits of HT / LT panels.
Cover was not provided on cable laying on floor in generator room | Provide adequate cable trenches with non-flammable covers at substation areas.
400kVA Generator room area was 23m2 which was not sufficient. | Modify Area of generator room to meet requirements of BNBC, the area shall be 48m2.
Proper working clearance was not available for maintenance. | Provide and maintain proper clearance in all sides of generator for ease of maintenance.
EXIT signage was not provided with proper illumination. | Exit signs may be illuminated either by lamps external to the sign or by lamps contained within the sign. The source of illumination shall provide not less than 50 lux at the illuminated surface with a contrast of not less than 0.5.
Single Line Diagram was not available in the factory. | a. Design to have proper segregation of different end used loads. b. Wiring design to have separate and distinct sub-circuits for power and heating system.
Ammeter & voltmeter was not adequate in LT panel & MDB. | Provide Ammeters / Voltmeters at distribution boards (LT/MDBs). Accuracy of the meter should be checked at regular interval by a standard calibrated meter
Cable sockets at cable end were not provided to stranded Cables with cable size, area >= 6mm2 | All stranded conductors \to be provided with cable sockets.
Cable / wire were found exposed or open live. | All strands cables at exposed ends shall be properly soldered / crimped and insulated.
Factory does not have overload protection in LT panel (COS) | Provide circuit breaker (MCCB) at all LT panels. Ensure that all LT panles shall have overload, short circuit protections and isolations in the circuits.
Energy meter was not installed at a convenient height with protection | Energy meters shall be installed at convenient height (At least 1.5 m above ground) with proper protection.
Adequate emergency power capacity was not available for essential lighting. | Review capacity of standby generator on basis of loads for essential lighting / Services. Replace generator with larger capacity or install second generator if review indicates existing unit is too small.
Inflammable materials were found near distribution board. | a. Remove all the inflammable materials from surrounding of electrical circuitry at MDBs/SDBs. b. Ensure that all electric circuitry clean of inflammable materials. c. Conduct periodic maintenance and maintain the records.
Circuit breaker located outside the building was exposed to weather without weather proof outer casing. | Provide weather proof casing for switchboards exposed to weather (located outside the building).
Area around open type switchboards was not properly ventilated. | Relocate the open type switchboards in dry / ventilated areas, away from batteries / chemical fumes.
Insulated support was not provided for high overhead service entries | a. Overhead service connections shall be covered and meet the requirements mentioned in BNBC Guidelines. b. Provide supports for main service line complete with adequate insulation.
Proper signage of Danger / 415 V on electrical panels was not present. | The electrical panels to be of metal case and shall be marked with “Danger 415 Volts” and identified with proper phase marking and danger signage.
Distribution board was not installed at accessible location. | Provide and maintain easy access and proper height of switchboard / panelboards ( < 2m from floor level).
Over current protection device was not installed for outgoing circuit. | Over current protection devices (Circuit breakers) shall be installed at all distribution panels.
Proper working clearance was not provided near distribution panels. | Provide proper clearance of in front of all distribution panels/switchboards.
Switchboards / panel boards made by flammable material (wood). | a. Wooden switchboards / panel boards shall be replaced by non-flammable materials. b. Prefer switchboards made of non-flammable materials.
Electrical connections were not properly secured with lugs and glands. | Provide cable connections with properly soldered / welded lugs at (LT/MDB/DB/SDB)'s. Ensure that all the electrical connections are properly secured with lugs and glands.
Wiring systems were not selected and erected properly. | a. Provide IP degree of protection to wiring system to protect the wiring circuit from ingress of water b. Ensure that all the wiring network shall have provisions to prevent the ingress of water in to the electrical wiring system.
Single Line Diagram was not available in the factory. | Select conductors with adequate sizing without exceeding permissible thermal limits for insulation.
Looping/Bunching at MCCB/busbar terminal was observed in the panels. | Avoid looping and bunch of cable at MCCB/MCB or bus bar terminal, use individual circuit and over current device for every incoming and outgoing circuit at the distribution boards.
Wiring diagram/ circuit list with proper current ratings were not available on every distribution boards. | Provide circuit diagram /circuit list with proper current ratings and fuse size, marking for DBs identifying end use, voltage, no. of phases.
Nonstandard cable joints was observed in electrical circuit. | Provide cable joints of porcelain / PVC connectors with PIB tape wound around before placing the cable in the box.
Common neutrals was observed for more than one circuit. SLD was not available. | Each circuit shall have a separate neutral (use of common neutral for more than one circuit shall not be permitted).
Fixed machines were wired with flexible cable or cords | a. Replace all flexible cables/wires with fixed wiring. avoid use of flexible wires/cords for fixed machines. b. Flexible cords may only be used for the connections of portable equipments.
Electrical wiring was not properly covered in conduit pipes. | Provide the wiring in PVC conduits or in metallic GI pipes. Ensure that all electrical wiring shall be covered in proper conduit pipes
Cable entry-exit point to the panel was not properly sealed | Seal the cable entry-exit points of (LT/MDB/DB/SDB)'s with non-flammable materials. In addition: a. Ensure that HT / LT panels / Switchgears to be vermin / damp proof. b. Ensure all unused holes / openings in DBs to be blocked properly.
Cables were taken improperly without protection in the factory. | Relocate the cables /wiring from damaged /chemically affected area. Ensure that all cables shall be away from areas where they can be damaged or chemically affected.
Proper grounding / earthing of generator was not provided | Provide proper separate earthing/grounding to generator. Ensure that generator body frame to have two separate and distinct connections to the earth / ground.
Single Line Diagram was not available in the factory. | a. Provide sufficient and separate earthing for HT / LT panels in substation/transformer room b. Provide adequate number of earth electrodes.
Earth Continuity Conductor (ECC) was not adequate and dedicated. SLD was not available. | a. Provide the ECC to meet minimum cross-sectional area as per standard. b. Ensure that connections between conductors / equipments provided to durable electrical continuity and adequate mechanical strength and protection. c. The continuous earth connection is provided back to the main intake supply earth.
Earthing was not provided on all electrical equipments. | Provide separate earthing connection to electrical equipments. Ensure that earth potential provided for all parts of equipment / installation (other than live parts) and that continuous earth connection is provided back to the main intake supply earth.
Earthing was not provided to all distribution board for its body & door | Provide adequate earthing to body and doors to all MDBs / DBs. Ensure that all electrical panels provided with proper and separate earth potential.
Lightning protection system was not available | Provide adequate protection against lightning depending on the probability of a strike and acceptable risk levels.
Lightning protection system was not available | Need to provide Lightning protection system with separate earthing. Ensure that this earthing shall be separate from other earthing system.
Periodical inspection and testing for insulation, earth resistance, operation test of equipments were not done. | Conduct Planned Periodical inspection and testing (insulation, earth resistance, operation test) of all electrical equipment to ensure proper operability of the installation and record shall be maintained.
Overloading or abnormal temperature was observed. | a. Disconnect loads with signs of overloading / abnormal temperature. b. Make necessary repairs to avoid accidents.