## Sheet1
গণপ্রজাতন্ত্রী বাংলাদেশ সরকার
শ্রম ও কর্মসংস্থান মন্ত্রণালয়
কলকারখানা ও প্রতিষ্ঠান পরিদর্শন অধিদপ্তর
প্রতিষ্ঠানসমূহের তালিকা
কারখানার নাম | জেমস নিটওয়ার (প্রাঃ) লিমিটেড।
কারখানার ঠিকানা | 15-16, New Jurain, Haji Habib ullah Super Market,Postagola, Dhaka-1204
মূল্যায়নের ধরণ | কাঠামোগত মূল্যায়ন
মূল্যায়নের তারিখ | ৩০-০১-২০১৫
পর্যবেক্ষণের তারিখ
পরিদর্শন পর্যবেক্ষণ | কর্ম পরিকল্পনা | চূড়ান্ত কর্ম পরিকল্পনা | চূড়ান্ত সময়রেখা | মন্তব্য | অগ্রগতির অবস্থা
Over stress has been found in central, corner and edge columns. | Loading should be reduced at 1KN/m2 (20 psf) as the edge (H/1) column is overstress. | We have reduced load as report recommendation | 22-06-2016 | on 29.05.18. In their task force meeting the factory management was suggested to do Dynamic analysis and resubmit to DIFE as soon as possible. On 10.11.2020: Dynamic analysis is not submitted yet. On 14/01/2021: There was no overloading has been found on the date of inspection. On 09/09/2021: There was no overloading has been found on the date of inspection. | চলমান
Over stress has been found in central, corner and edge columns. | Factory Engineer to review design, loads and columns stresses in the area identified above. Verify in situ concrete stresses either by 100mm dia. cores or existing cylinder strength data for [the identified columns] or [100mm dia. cores from 4 columns]. Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. A Detail Engineering Assessment of Factory to be commenced. See attached Scope at Chapter 6. | We already engaged a consulting firm for our work | 27-07-2016 | on 29.05.18. In their task force meeting the factory management was suggested to do Dynamic analysis and resubmit to DIFE as soon as possible. On 10.11.2020: 100mm dia Core test has been completed as a part of DEA. On 14/01/2021:Factory management submitted their DEA report to DIFE for approval. On 09/09/2021: Factory management submitted their DEA report to DIFE for approval. They are advised to re-submit their documents with some additional requirments but not submitted yet. | চলমান
Over stress has been found in central, corner and edge columns. | Continue to implement load plan. | We will follow our DEA Report | 15-12-2016 | on 29.05.18. In their task force meeting the factory management was suggested to do Dynamic analysis and resubmit to DIFE as soon as possible. On 10.11.2020: Load plan has been submitted to DIFE with DEA on 29.05.2018. On 14/01/2021::Load plan has been submitted to DIFE for approval. No load management program has been found on site. On 09/09/2021: Load plan has been submitted to DIFE for approval. No load management program has been found on site. | চলমান
Non engineering Shed—Storage and prayer room on the roof top are constructed without design documents. Roof of sheds are not properly designed and bolted adequately. | Prepare design documents with detailed calculation by qualified structural engineer. Building engineer to assess light weight roof structure and confirm its ability to withstand all wind loading pressure, suctions and uplift forces. A Detail Engineering Assessment of Factory to be commenced. See attached Scope at Chapter 6. | After DEA completed we will take action as per DEA recommendation. | 27-06-2016 | on 29.05.18. In their task force meeting the factory management was suggested to do Dynamic analysis and resubmit to DIFE as soon as possible. On 10.11.2020: Non engineering shed already removed. Some room exists but not functional. On 14/01/2021::Factory management submitted their DEA report, As built Structural & Architectural drawing to DIFE for approval. On 09/09/2021: Factory management submitted their DEA report, As built Structural & Architectural drawing to DIFE for approval. | চলমান
Non engineering Shed—Storage and prayer room on the roof top are constructed without design documents. Roof of sheds are not properly designed and bolted adequately. | Need to prepare design drawing as per chapter 6 of this report by qualified structural engineer. | Do | 15-12-2016 | On 10.11.2020: Non engineering shed already removed. Some room exists but not functional. It will be removed soon. On 14/01/2021::Factory management submitted their DEA report, As built Structural & Architectural drawing to DIFE for approval. On 09/09/2021: Factory management submitted their DEA report, As built Structural & Architectural drawing to DIFE for approval. | চলমান
Over loaded material storage (Yarn) on the 1st floor (stack height 8’-0” ft., loading 100 psf). | Factory Engineer to review design loads, floor, Beam and column capacity and limit the height of the stack within design capacity. | We have removed additional goods | 27-07-2016 | On 10.11.2020: No overload has been observed during inspection day. Factory management submitted their DEA report, As built Structural & Architectural drawing,floor load plan to DIFE for approval. On 14/01/2021: There was no overloading has been found on the date of inspection. On 09/09/2021: There was no overloading has been found on the date of inspection. | সংশোধিত
Over loaded material storage (Yarn) on the 1st floor (stack height 8’-0” ft., loading 100 psf). | Continue to implement load plan and manage floor loading. | Do | 15-12-2016 | 12.02.20 visit observation : They submitted their Floor load plan to DIFE on 29.05.18 In their task force meeting the factory management was suggested to do Dynamic analysis and resubmit to DIFE as soon as possible. On 10.11.2020: No overload has been observed during inspection day. On 09/09/2021: There was no overloading has been found on the date of inspection but no load management program has been found on site. | সংশোধিত
Water tanks found on the several spans of the roof top slab. In total 9 nos. 2000 liter, 1 no. 500 liter water tanks have been found. However, noticeable cracks have been found due to the loads of water tanks on the beams or slabs below roof. | Building Engineer to ensure the structure is not loaded beyond capacity by the loading from the water tank. | We have already started | 27-07-2016 | 12.02.20 visit observation :The factory management relocate the position of water tank and there are 5 nos. 2000 liter water tank at roof observed by RCC engineer. On 10.11.2020: 3 Nos of 2000 litre water tank has been shifted. On 14/01/2021: 3 Nos of 2000 litre water tank has been shifted. On 09/09/2021: 3 Nos of 2000 litre water tank has been shifted. | সংশোধিত
Water tanks found on the several spans of the roof top slab. In total 9 nos. 2000 liter, 1 no. 500 liter water tanks have been found. However, noticeable cracks have been found due to the loads of water tanks on the beams or slabs below roof. | Relocate water tanks around building to distribute the concentrated loads more efficiently, if required. | Do | 15-12-2016 | On 14/01/2021: 3 Nos of 2000 litre water tank has been shifted. On 09/09/2021: 3 Nos of 2000 litre water tank has been shifted. | সংশোধিত
Several minor cracks have been observed in the 4th floor beams due to the load of additional structure on the roof of observation 4. | Building Engineer to review further if cracks are found to penetrate into building structure. Prepare calculations showing the structural adequacy of the building structure taking into account the factory design imposed loading and the as built structure. A Detail Engineering Assessment of Factory to be commenced. See attached Scope at Chapter 6. | We already repaired all cracks | 27-07-2016 | On 10.11.2020: Hairline crack has been found on 3rd floor beam And other different structural areas. On 14/01/2021:Factory management submitted their DEA report to DIFE for approval but no investigation report has been found on site for crack. On 09/09/2021: Factory management submitted their DEA report to DIFE for approval but no investigation report has been found on site for crack. | চলমান
Several minor cracks have been observed in the 4th floor beams due to the load of additional structure on the roof of observation 4. | Building engineer to record all cracking throughout building and monitor on an on-going basis. | Do | 15-12-2016 | On 10.11.2020: Hairline crack has been found on 3rd floor beam And other different structural areas. On 14/01/2021:No investigation report has been found on site for crack. On 09/09/2021: No investigation report has been found on site for crack. | শুরু হয়নি
North-West corner of the building, which was not part of the RMG industry, was under demolition of walls by the building owner. The building owner decided to renovate the north-west portion for future rental purpose. Though the dismantle works was limited to masonry walls, perhaps, proper caution is required so that structural component such as—columns and beams might not be distressed by unintentional hammer strike. | Need to provide adequate shuttering and props to conduct safer demolition. | We have stopped all kind of demolition work | 22-06-2016 | 12.02.20 visit observation : Building's owner already demolished that portion, but they do not clear the rubbish, also garment's owner does not represent any interest to clear that section. On 10.11.2020: North-west corner of building is not fully demolished. On 14/01/2021:Building's owner already demolished that portion, but they do not clear the rubbish. On 09/09/2021: Building's owner has demolished that portion, | চলমান
North-West corner of the building, which was not part of the RMG industry, was under demolition of walls by the building owner. The building owner decided to renovate the north-west portion for future rental purpose. Though the dismantle works was limited to masonry walls, perhaps, proper caution is required so that structural component such as—columns and beams might not be distressed by unintentional hammer strike. | Conduct the masonry demolition works under supervision of qualified engineer. | Do | 27-07-2016 | On 14/01/2021:Building's owner already demolished that portion, but they do not clear the rubbish. On 09/09/2021: Building's owner already demolished that portion, but there is no observation report is found. | চলমান
Dampness and water ponding have been observed on the roof area. | It is advisable to locate leaks and remove them. Engineer to inspect water damaged structure and propose a suitable repair. | We have repaired all kind of leaks | 27-07-2016 | On 10.11.2020: water ponding of roof has been found. On 14/01/2021: Water ponding and vegetation has been found on roof. On 09/09/2021: Water ponding and vegetation has been found on roof. | চলমান
Dampness and water ponding have been observed on the roof area. | For both durability and serviceability, waterproofing on the roof slab is recommended. Moreover the roof slab drainage system should be investigated periodically. | We have provided drainage system for drain out | 15-12-2016 | On 10.11.2020: water ponding of roof has been found. On 14/01/2021:Water ponding and vegetation has been found on roof. On 09/09/2021: Water ponding and vegetation has been found on roof. | চলমান
Severe dampness have been found on the some portion of the roof of 4th floor and wall of 2nd, 3rd and 4th floor. Perhaps, dampness and water ponding on roof top, leakage of internal pipes near toilet zone are the causes of dampness. | Remedial action to be undertaken to prevent the seepage of water from pipes and other sources. | We are working for this issue | 27-07-2016 | On 10.11.2020: Dampness have been observed in severel areas. On 14/01/2021:Dampness has been found on almost all the floors at periphery wall & slab. On 09/09/2021:Dampness has been found on almost all the floors at periphery wall & slab. | শুরু হয়নি
Severe dampness have been found on the some portion of the roof of 4th floor and wall of 2nd, 3rd and 4th floor. Perhaps, dampness and water ponding on roof top, leakage of internal pipes near toilet zone are the causes of dampness. | Causes of Dampness and remedial action should be monitored on ongoing basis. |  | 15-12-2016 | 12.02.20 visit observation : 12.02.20 visit observation :Severe dampness have been found on the wall of 4th floor and 3rd floor by RCC engineer. On 10.11.2020: water ponding of roof has been found. On 14/01/2021:Dampness has been found on almost all the floors at periphery wall & slab. On 09/09/2021: Dampness has been found on almost all the floors at periphery wall & slab. | শুরু হয়নি
6” extra slab casting on the machinery section (washing, dryer, hydro) of the 2nd floor. However, position of extra slab is not in the same of critical columns, since, columns near this zone have smaller contributory area and spans on other successive floor levels are seem to be lightly loaded. | Confirm the effects of extra loading by qualified structural engineer. | After DEA completed we will take action as per DEA recommendation. | 22-06-2016 | on 29.05.18 In their task force meeting the factory management was suggested to do Dynamic analysis and resubmit to DIFE as soon as possible. On 10.11.2020: This issue is part of DEA and DEA has been submitted to DIFE but requred dynamic analysis is not submitted yet. On 14/01/2021:Factory management submitted their DEA report to DIFE for approval. On 09/09/2021: Factory management submitted their DEA report, As built Structural & Architectural drawing to DIFE for approval. | চলমান
6” extra slab casting on the machinery section (washing, dryer, hydro) of the 2nd floor. However, position of extra slab is not in the same of critical columns, since, columns near this zone have smaller contributory area and spans on other successive floor levels are seem to be lightly loaded. | Factory Engineer to review design, loads and columns stresses in area identified above as part of DEA. | Do | 27-07-2016 | On 10.11.2020: This issue is part of DEA and DEA has been submitted to DIFE but requred dynamic analysis is not submitted yet. On 14/01/2021:Factory management submitted their DEA report to DIFE for approval. On 09/09/2021: Factory management submitted their DEA report, As built Structural & Architectural drawing to DIFE for approval. | চলমান
6” extra slab casting on the machinery section (washing, dryer, hydro) of the 2nd floor. However, position of extra slab is not in the same of critical columns, since, columns near this zone have smaller contributory area and spans on other successive floor levels are seem to be lightly loaded. | Continue to implement load plan if necessary. | Do | 15-12-2016 | On 10.11.2020: This issue is part of DEA and DEA has been submitted to DIFE but requred dynamic analysis is not submitted yet. On 14/01/2021: There was no overloading has been found on the date of inspection but no load management program has been found on site. On 09/09/2021: There was no overloading has been found on the date of inspection but no load management program has been found on site. | চলমান